# M2T — Meter-to-Transformer Mapping Model

Meter-to-Transformer Mapping: Technical Reference Guide

Internal Engineering / Data Team | Confidential

# 1. Overview

The M2T model identifies which secondary distribution transformer each single-phase electric meter is connected to, by correlating the meters' voltage signatures over time. It is built to validate and improve the GIS-side meter↔transformer assignments by surfacing meters whose voltage behavior is inconsistent with their currently-assigned transformer.

The model is designed to stand alone as a peer to GIS, not as a downstream consumer of it. The known_mapping (built from the GIS ServicePoints file) is treated as one source of truth; the model is treated as another. When they disagree, the disagreement itself is the signal worth investigating.

# 2. Quick Start (Weekly Run)

cd <project-root>

Standard weekly run sequence. Start in the project root and optionally refresh GIS source files before advancing the rolling window.

If you received new ServicePoints*.csv or Transformers*.csv files, drop them into GIS_mapping\ before rebuilding the known mapping.

# 1. Pull new daily parquet files and refresh GIS data (optional)
# Drop new ServicePoints*.csv or Transformers*.csv into GIS_mapping/ if you got one.

# 2. Slide the rolling window forward one day at a time
python rolling_update.py "data\raw\daily\<YYYY-MM-DD>.parquet"
# ... repeat per new parquet day ...

# 3. Refresh the GIS-derived truth file (if you added a new ServicePoints CSV)
python build_known_mapping.py

# 4. Run the model
python rerun_clustering.py
python find_mapping_errors.py
python evaluate_results.py
python rank_corrections.py

# 5. Persist this run and produce enriched / stability-scored outputs
python record_run.py <YYYY-MM-DD>_<label>
python stability_report.py
python enrich_outputs.py

# 6. Compare against a prior baseline
python compare_runs.py "data\<some_baseline_folder>"

ⓘ First-Time Setup If no signature store exists yet, run python build_signature_store.py once with at least WINDOW_DAYS (currently 45) daily parquets in data\raw\daily\ before starting the weekly cycle.

# 3. Pipeline Architecture

Detailed description of each pipeline stage.

## 3.1 Extract

save_daily_data.py runs the SQL in db_oracle.py against C2M for each hour of each requested day, writing one parquet per day to data\raw\daily\. Each row is one meter's 15-minute voltage measurement converted to per-unit (PU) using the nominal voltage implied by the meter's device type.

## 3.2 Build / Roll the Signature Store

build_signature_store.py assembles a memmapped float32 matrix of shape (n_badges × WINDOW_DAYS × INTERVALS_PER_DAY). Each row is one meter's per-unit voltage signature across the rolling window (currently 4,320 points = 45 days × 96 fifteen-minute slots). rolling_update.py slides the window forward by one day at a time: drops the oldest day, appends the newest.

## 3.3 Spatial Filter

spatial_neighbors.py builds a haversine BallTree and, for each meter, returns the indices of all other meters within RADIUS_METERS (default 175 m). This is purely a candidate filter; the radius does not enter the correlation math.

## 3.4 Correlation

correlation_engine.py runs pairwise Pearson correlation on the full 4,320-point signatures of candidate pairs. Requires at least MIN_OVERLAP_POINTS non-NaN overlapping samples (default 4,000 ≈ 70% data presence). Pearson is scale- and offset-invariant, so what's being matched is the shape of the load signature, not its magnitude.

## 3.5 Edge Filtering

edge_builder.py keeps only pairs with correlation ≥ CORRELATION_THRESHOLD (currently 0.95), then trims to each node's top TOP_K_NEIGHBORS (currently 5), then requires the relationship to be mutual — both meters must rank each other in their top-K. This is a strong noise rejector.

## 3.6 Cluster

clustering_engine.py builds an undirected graph from the surviving mutual edges and returns connected components. rerun_clustering.py orchestrates steps 3–6 and writes data\outputs\full_clusters.csv.

## 3.7 Compare Against GIS

find_mapping_errors.py joins clusters with known_mapping.csv, finds each cluster's majority transformer (by mapped-peer vote), and flags any meter whose assigned transformer differs from the majority. evaluate_results.py reports cluster purity and transformer completeness summary statistics.

## 3.8 Score and Rank

rank_corrections.py adds confidence_gap and majority_share columns. record_run.py appends this run to the stability ledger. stability_report.py computes peer-co-membership and recommendation-consistency scores across all recorded runs. enrich_outputs.py adds GIS context columns (address, feeder, transformer location, distances, mismatch classification) and builds supplementary reports.

# 4. Output Files

Output files are organized by priority. Use the primary outputs for operational work; reference outputs support deeper investigation.

## 4.1 Primary Outputs

| File | Rows (typical) | What it is | Use it for |
| --- | --- | --- | --- |
| corrections_high_confidence_enriched.csv | ~1,800 | Recommendations passing all four gates: cluster confidence_gap ≥ 0.5, mapped peers ≥ 4, peer stability ≥ 0.7, recommendation stability ≥ 0.7 | The field-team work list. Sort by RECOMMENDATION_TYPE. |
| corrections_with_stability_enriched.csv | ~12,000 | Every flagged correction + stability scores + GIS context | Lower-bar review and deeper audits |
| badges_missing_from_gis.csv | ~125 | Badges in your model with no GIS row | Push to GIS team — gaps to add |
| latlon_discrepancies.csv | ~1,300 | Badges where model lat/lon differs from GIS by >100 m | Push to GIS team — data quality candidates |
| full_clusters_enriched.csv | ~218,000 | Every badge with cluster ID + GIS context (address, X/Y, feeder, GIS transformer) | Downstream mapping / analytics joins |

## 4.2 Reference Outputs

| File | What it is |
| --- | --- |
| full_clusters.csv | Bare badge → cluster ID assignments (source of truth for cluster membership) |
| known_mapping.csv | Generated from latest ServicePoints; the truth file the model compares against |
| cluster_to_transformer_counts.csv | Per cluster: distinct transformer count. 1 = clean cluster. |
| transformer_to_cluster_counts.csv | Per transformer: cluster count it spans. 1 = clean transformer. |
| badge_stability_summary.csv | Per-badge stability metrics (useful for dashboards) |
| excluded_missing_coords.csv | Badges excluded for missing lat/lon — should be empty in healthy runs |

## 4.3 Intermediate Outputs (Rarely Opened Directly)

| File | What it is |
| --- | --- |
| transformer_corrections.csv | Raw model recommendations before suppression/enrichment |
| corrections_ranked.csv | Raw recommendations sorted by confidence |
| corrections_with_stability.csv | Recommendations + stability columns, no GIS context |
| corrections_high_confidence.csv | Pre-enrichment subset |
| transformer_corrections_enriched.csv, corrections_ranked_enriched.csv | Enriched but pre-stability (use corrections_high_confidence_enriched.csv instead) |
| corrections_suppressed.csv | Recommendations suppressed via data\state\corrections_ignored.csv |

## 4.4 Comparison Run Subfolders (comparison_<timestamp>\)

Created by compare_runs.py. Contains the following files:

| File | What it is |
| --- | --- |
| summary.txt | Printed comparison report |
| badge_cluster_changes.csv | Badges that moved between cluster assignments across runs |
| old_clusters_that_split.csv | Clusters from the baseline run that fragmented in the new run |
| new_clusters_that_merged.csv | Clusters in the new run that absorbed previously separate clusters |
| transformer_corrections_diff.csv | Difference in transformer correction recommendations between runs |

# 5. Run Metrics — What They Mean

At the end of each run, evaluate_results.py and rank_corrections.py print the headline numbers worth quoting in summary emails and comparing across runs.

## 5.1 Cluster Purity

Cluster purity measures what percentage of produced clusters contain meters from only one transformer according to GIS. A cluster where all badges map to the same transformer is pure; a cluster mixing badges from different GIS transformers is impure. This is the “no false merges” metric. Higher is better, and typical runs land around 91–94% because the mutual top-K filter is naturally good at avoiding merges between genuinely different signatures.

## 5.2 Transformer Completeness

Transformer completeness measures what percentage of GIS transformers have all of their meters grouped into a single cluster. If one transformer’s meters are split across multiple clusters, completeness falls. This is the “no false splits” metric. Higher is better, but it usually has more room to improve because noise, sparse data, and geographic separation can cause true peers to miss the mutual top-K cut and fragment across clusters.

## 5.3 How Purity and Completeness Relate

- Tighten threshold — purity increases, completeness decreases: cleaner clusters, more fragmentation.

- Loosen threshold — purity decreases, completeness increases: bigger clusters, but more mixing.

- Ideal state — both near 100%: every cluster corresponds to one transformer and every transformer collapses to one cluster.

A run with purity 93% and completeness 44% means that when the model groups meters, it is usually right that they belong together, but it is still missing many true same-transformer connections.

# 6. Triage Priority in Plain English

If a field tech asks which recommendations to investigate first, use this priority order:

- High-confidence + cross_feeder_likely_gis_error — strongest possible signal.

- High-confidence + new_assignment — strong first-time GIS assignment candidates.

- Strong-signal + cross_feeder_likely_gis_error not yet in the high-confidence list — worth investigating on a slower timeline while more run history accumulates.

- Anything same_feeder_ambiguous — last priority; treat as field-validation candidates only.

# 7. RECOMMENDATION_TYPE Values

## 7.1 CONFIDENCE_GAP

Per correction, CONFIDENCE_GAP = (MAJORITY_VOTES − CURRENT_VOTES) / MAPPED_PEERS. It measures how much more strongly the cluster votes for the recommendation than for the badge’s current GIS assignment, normalized by the number of mapped peers. A gap of 0.0 is a bare majority, 0.5 is a strong lead, and 1.0 is unanimous.

## 7.2 Strong-Signal

A correction is considered strong-signal when it satisfies two single-run quality filters: CONFIDENCE_GAP >= 0.5 and MAPPED_PEERS >= 4. This is a snapshot filter: it looks only at this run’s evidence, not history.

## 7.3 High-Confidence and the Four Gates

| Gate | Threshold | What it checks |
| --- | --- | --- |
| 1 | CONFIDENCE_GAP >= 0.5 | Strong majority lead in this run’s cluster vote. |
| 2 | MAPPED_PEERS >= 4 | Enough peers contributed to the vote. |
| 3 | PEER_STABILITY >= 0.7 | The peer group is stable across recorded runs. |
| 4 | RECOMMENDATION_STABILITY >= 0.7 | The same badge → transformer recommendation recurs across runs. |

Passing all four gates means the model is making the same strong recommendation, backed by the same stable peer group, in run after run. That is the most actionable output, and corrections_high_confidence_enriched.csv is the file field operations should work from.

Each enriched correction carries one of four labels reflecting how to interpret it. Sort priority work by this column first.

| Value | Meaning | How to Triage |
| --- | --- | --- |
| cross_feeder_likely_gis_error | Current and recommended transformers are on different feeders | High signal. Voltage signatures shouldn't cross feeders, so the parsimonious read is that GIS has the badge on the wrong feeder/transformer. |
| new_assignment | Badge has no current transformer in GIS | Easy win. Push these to the GIS team as first-time assignment candidates. |
| same_feeder_ambiguous | Both transformers on the same feeder | Lower signal. Same-feeder meters share upstream voltage; signatures can match across genuinely-different transformers. Combine with high stability AND field validation before acting. |
| unknown_feeder | Feeder data missing for one or both transformers | Flag the underlying transformer to GIS to fill in feeder data; re-evaluate next run. |

# 8. About the Model's Confidence Limits

Voltage-signature correlation has a fundamental ceiling on what it can distinguish. Two transformers sharing an upstream feeder, especially adjacent ones in residential subdivisions, can produce voltage signatures that look identical to the model. Field validation has confirmed this in practice.

The same_feeder_ambiguous label is the model's way of saying: "I have a recommendation but I can't reliably verify it from voltage alone."

⚠ Important — Know the Ceiling Do not action same_feeder_ambiguous corrections based on model output alone. Adjacent same-feeder transformers in residential subdivisions routinely produce near-identical voltage signatures. Always combine these with high stability scores and physical field validation before treating the recommendation as actionable.

# 9. Configuration (config.py)

The following parameters control model behavior. Edit config.py to tune thresholds.

| Parameter | Current Value | Effect |
| --- | --- | --- |
| WINDOW_DAYS | 45 | Length of the rolling signature window in days |
| INTERVALS_PER_DAY | 96 | 15-minute intervals per day |
| SIGNATURE_LENGTH | 4,320 | WINDOW_DAYS × INTERVALS_PER_DAY |
| RADIUS_METERS | 175 | Geographic candidate filter; not part of correlation math |
| CORRELATION_THRESHOLD | 0.95 | Minimum Pearson r for an edge to form |
| MIN_OVERLAP_POINTS | 3,000 | Minimum non-NaN overlapping samples to compute correlation |
| TOP_K_NEIGHBORS | 5 | Maximum candidate edges per node before the mutual filter |
| EARTH_RADIUS_M | 6,371,000 | Used in haversine distance calculation |
| MAX_RETRIES | 3 | SQL extraction retry count |

## 7.1 Window-Length Tradeoffs (Empirical)

- 30 days — least seasonal mixing; tightest threshold-sensitivity

- 45 days — middle ground; modest improvement on transformer completeness

- 45 days (current) — more statistical power per pair but spans winter→spring transitions

- >60 days — marginal benefit, real seasonal drift risk; not recommended

## 7.2 Threshold Tradeoffs

- Lower threshold (e.g. 0.93) — more edges form, fewer fragmented transformers, more bridge-error risk

- Higher threshold (e.g. 0.97) — cleaner clusters, more singletons, more fragmentation

# 10. Stability Ledger (data\state\history\)

Each run is recorded into a persistent ledger so we can score how consistent the model is across runs.

| File | What it contains |
| --- | --- |
| runs.parquet | One row per recorded run (RUN_ID, RUN_DATE, badge/cluster counts) |
| badge_presence.parquet | Per-badge appearance counts across all runs |
| pair_co_membership.parquet | Per-pair (BADGE_A, BADGE_B) co-cluster counts |
| recommendation_history.parquet | Per (BADGE, RECOMMENDED_TRANSFORMER) recommendation counts |

stability_report.py reads the ledger and produces two key metrics:

- PEER_STABILITY — For each badge's current peers, what fraction of runs have they actually been peers? High = the cluster is stable across runs.

- RECOMMENDATION_STABILITY — For each (badge, recommended_transformer) pair, what fraction of runs has produced this same recommendation? High = the model has been consistent in flagging this.

ⓘ Note The first ~5 runs are when stability scores become meaningful. Weekly cadence is recommended for accumulating runs.

# 11. Suppression List (data\state\corrections_ignored.csv)

A user-maintained CSV with columns BADGE, RECOMMENDED_TRANSFORMER, DATE_ADDED, NOTES. Any (BADGE, RECOMMENDED_TRANSFORMER) pair listed here is suppressed from transformer_corrections.csv going forward — it appears in corrections_suppressed.csv for audit instead.

The match is on the pair — if the model later recommends a different transformer for the same badge, the new recommendation still surfaces.

# 12. GIS Source Files (GIS_mapping\)

⚠ Not in Repository These files are not committed to the repo due to file size (ServicePoints is ~200 MB and). Place the latest files in GIS_mapping\.

| File Pattern | Description | Key Fields Used |
| --- | --- | --- |
| ServicePoints*.csv | Every electric meter with its badge and transformer-bank references. The loader is schema-adaptive: it accepts both the legacy CSV format and the newer Power BI / Fabric dataflow export. | BADGENUMBER, SPID, TRANSFORMERBANKOBJECTID, POINT_X/Y (or SP_X/Y), CCBADDRESS1, CCBCITY, FEEDERID; TRANSBANKTAG and d_FEEDERID used when present |
| Transformers*.csv | Transformer metadata. Loader prefers the OBJECTID join to ServicePoints (100% coverage on the current dataflow), and falls back to the TAG join for legacy files. A fallback decoder from prior extracts fills in STRUCTNO / TAG / d_FEEDERID / d_SUBTYPECD for transformers already known when those columns are absent from the current file. | OBJECTID (preferred) or TAG, LID, VAULTCD, FEEDERID, TOTALKVA, POINT_X/Y (or XFER_X/Y); STRUCTNO, d_FEEDERID, d_SUBTYPECD used when present |

Both build_known_mapping.py and enrich_outputs.py pick the most-recently-modified files matching their respective glob patterns, so when GIS sends a new file just drop it in and re-run.

# 13. Dependencies

- numpy

- pandas

- pyarrow

- scikit-learn

- networkx

- oracledb (only needed on the machine that runs save_daily_data.py)

Install with:

pip install numpy pandas pyarrow scikit-learn networkx

Or if a requirements file is present:

pip install -r requirements.txt

# 14. Troubleshooting

# Appendix A. Current Run Metrics

Headline run metrics move week-over-week and are maintained in the stakeholder-facing executive update rather than in this reference. For the most recent numbers — total clusters, cluster purity, transformer completeness, flagged/high-confidence counts, recommendation-type breakdown, badges missing from GIS, lat/lon discrepancies, and consensus tier counts — see the current M2T Executive Update document distributed alongside this reference.

The executive doc's Section 2 (Latest Metrics) is the authoritative source for those numbers on any given run.

# Appendix B. Parallel Model, Consensus Reporting, and GIS Dataflow

Since the prior revision of this reference, the model has grown three architecturally significant additions. This appendix summarizes each; the config-driven parameters and operational commands for the production model in Sections 1–14 above still apply unchanged.

## B.1 Parallel Model (v2)

A second parallel model runs alongside the production model and consumes the same daily voltage parquets. Instead of computing a single Pearson correlation over a fixed rolling window, the parallel model maintains a per-pair ledger of daily Pearson values and applies stability gates to those values before edge formation. This means a pair's inclusion as a graph edge depends not just on today's correlation being high, but on the pair's daily correlations being consistently high, having low variance, and not trending downward.

Pipeline modules:

• pair_accumulator.py — persistent ledger of daily Pearson values per pair. Stores the last WINDOW_DAYS values plus cumulative statistics (n, historical mean, first/last day).

• daily_correlate.py — reads one daily parquet, computes per-pair daily Pearson correlations for all candidate pairs, and updates the ledger via the streaming update path.

• streaming_update.py — merges today's correlations into the on-disk ledger by streaming through Parquet chunks. Never loads the full ~12M-pair ledger into memory; peak memory ~500 MB regardless of ledger size.

• backfill_accumulator.py — replays a range of daily parquets through the streaming update path. Supports --resume, --from-date, and --to-date arguments.

• cluster_from_accumulator.py — applies the stability gates (minimum days, mean, standard deviation, trend), builds mutual top-K edges, and produces v2 clusters.

• run_v2_pipeline.py — orchestrates the v2 side of the weekly cadence: clustering, error detection, ranking, run recording, stability reporting, and enrichment.

Configuration for v2 gate thresholds is in config.py under the V2_* constants (V2_THRESHOLD, V2_STD_MAX, V2_TREND_MIN, V2_MIN_DAYS). Outputs land in data/outputs_v2/ and follow the same file naming and column conventions as the production outputs so downstream tooling works against either.

## B.2 Consensus Reporting

consensus_report.py compares the production and parallel models' high-confidence sets and produces data/outputs/consensus_report.csv with a CONSENSUS_TIER column. Tiers, in decreasing order of signal strength:

• both_high_confidence — both models independently pass all high-confidence gates on the same (BADGE, RECOMMENDED_TRANSFORMER) pair. Strongest possible signal from voltage data alone.

• v1_high_confidence_v2_seen — production model is high-confidence; parallel model has the same recommendation at lower confidence. Strong.

• v2_high_confidence_v1_seen — parallel model is high-confidence; production model has the same recommendation at lower confidence. Strong.

• v1_high_confidence_only / v2_high_confidence_only — one model is high-confidence and the other doesn't flag the pair. Moderate; investigate why the other model missed it.

• both_seen — both models flag the pair at lower-than-high confidence. Weak but worth tracking across runs.

• v1_only / v2_only — flagged by only one model. Weakest tier; treat as candidates rather than definite findings.

The consensus report is the recommended entry point for downstream triage. Filter to CONSENSUS_TIER = both_high_confidence AND RECOMMENDATION_TYPE = cross_feeder_likely_gis_error for the highest-signal subset.

## B.3 GIS Dataflow Integration

The model consumes GIS data from a Power BI / Fabric dataflow. The dataflow's output — ServicePoints and Transformers CSV exports — is dropped into GIS_mapping/, and the loader picks the most-recently-modified files automatically. The dataflow schema differs from the legacy file format in three ways:

• Coordinate columns are named SP_X/SP_Y (ServicePoints) and XFER_X/XFER_Y (Transformers) rather than POINT_X/POINT_Y. The loader auto-renames them to canonical POINT_X/POINT_Y at read time.

• The ServicePoints-to-Transformers join uses TRANSFORMERBANKOBJECTID → OBJECTID (100% match coverage) instead of the legacy TRANSBANKTAG → TAG join (~97% coverage). The loader prefers OBJECTID when available.

• Several decoded columns (d_FEEDERID, STRUCTNO, TAG, d_SUBTYPECD) are not present in the current dataflow export. The loader falls back to a per-key decoder built from the newest older file in GIS_mapping/ that contains them, filling in values for infrastructure already known at that snapshot. New infrastructure created after the decoder file's snapshot shows blank for those columns.

The intent is that when the dataflow owner adds the missing decoded columns back, no code change is required — the loader sees them and stops using the fallback decoder for those keys.

## B.4 Downstream Identifier Columns

Enriched output files now include three identifier columns requested by downstream users:

• BADGE_SPID — the meter's SPID from ServicePoints (per-service-point, badge-level).

• CURRENT_TX_LID — the LID of the meter's currently-assigned transformer (from Transformers, joined via TRANSFORMERBANKOBJECTID).

• RECOMMENDED_TX_LID — the LID of the transformer the model recommends the meter be reassigned to.

CURRENT_TX_VAULTCD and RECOMMENDED_TX_VAULTCD were already present in the enriched output and remain unchanged.